AUCOOP · Hospital Digitalisation Handbook · Instrument D-2

Infrastructure audit

While you are there   ·   Before departure, then first week on site

The status of every infrastructure requirement before Phase 1 goes live, with its evidence. Fill in before departure from what can be reported, then check each row on arrival.

| Hospital | Unit / area | Completed by | Date |
| --- | --- | --- | --- |

1. The audit — status: met / partly / not met / unknown

| Layer | Requirement | Minimum for Phase 1 | How to verify | Status | Evidence |
| --- | --- | --- | --- | --- | --- |
| Power | HIS equipment never on unprotected supply | Servers and network core on UPS | Trace each server and core device to its supply |  |  |
| Power | UPS energy from the critical load, with ageing factor | Time to shut down safely or bridge to the generator | Record the model and battery; measure runtime under load |  |  |
| Power | Battery replacement interval for the room temperature | Interval known and budgeted | Log the room temperature; record installation dates |  |  |
| Power | Supply voltage logged before choosing the UPS topology | One full day logged | Voltage logger at the supply point |  |  |
| Power | Solar sized for the worst month and the autonomy required | Supply covers working hours | Survey panels, controller, batteries and loads; redo the battery sizing |  |  |
| Location | Lockable cabinet, surge protection, room within the equipment's temperature range | Lockable cabinet; temperature within the servers' specification | Inspect the cabinet; log the room temperature |  |  |
| Network | Every unit using the system reaches the server | Each Phase 1 unit connected | Test from each unit's workstation |  |  |
| Network | Acceptable response time | Interactive response at every unit | Time typical actions in the system at the furthest units |  |  |
| Network | Cabling within standard limits | Runs within limits | Survey the cabled sections |  |  |
| Network | Segmentation with filtering | Documented, even if not yet implemented | Inspect router and switch configuration |  |  |
| Server | Platform requirements | 4 cores, 8 GB, 150 GB (Bahmni) | Inspect the hardware |  |  |
| Server | A second machine able to take over | Backup server | Restore a virtual machine onto it |  |  |
| Backup | 3-2-1, one copy off site, encrypted | Daily backup; encrypted off-site copy | Check the schedule, a recent backup and who holds the key |  |  |
| Recovery | Unattended recovery after a power cut | Shutdown on low battery; power-on on return; start order set | Cut the supply under supervision and observe |  |  |
| Recovery | Written downtime procedure; emergency paper forms; annual drill | Procedure written; forms for at least 8 h in each Phase 1 unit | Read the procedure; count the forms; run a drill |  |  |
| Remote access | Outbound VPN through carrier NAT | Remote access to the server | Connect from outside; record who holds the keys |  |  |
| Monitoring | Remote monitoring and alerts | An alert when the server stops | Stop a test service and confirm the alert |  |  |

Rows found unknown or not met are the first tasks of the trip. Requirements and sources: companion thesis §7.10.

2. Inputs — Electricity

| Item | Finding | Source / photo |
| --- | --- | --- |
| Grid hours/day (observed) |  |  |
| Generator: fuel / capacity / manual or automatic start |  |  |
| Solar: panels, controller, battery capacity, chemistry, installation date |  |  |
| Voltage logged over a full day (min / max / typical) |  |  |
| Outlet locations per building |  |  |

3. Inputs — Internet

| Item | Finding | Source / photo |
| --- | --- | --- |
| Provider and technology |  |  |
| Contracted bandwidth |  |  |
| Measured bandwidth (down / up, time of day) |  |  |
| Carrier-grade NAT check: router WAN address vs public address |  |  |
| Monthly cost |  |  |

4. Inputs — Space and environment

| Item | Finding | Source / photo |
| --- | --- | --- |
| Equipment room: ventilation / lock / keyholder / temperature |  |  |
| Cable routes between buildings; anything crossing open ground or a road |  |  |
| Distance between the farthest buildings; wall materials |  |  |
| Humidity, dust, insects and rodents, flooding |  |  |
| Lightning: frequency, existing protection |  |  |

5. Inputs — Existing IT

| Item | Finding | Source / photo |
| --- | --- | --- |
| Computers and tablets (count, OS, age) |  |  |
| Printers |  |  |
| Network equipment (models, where, working?) |  |  |
| Existing cabling |  |  |
| Existing software (finance, forms, earlier projects) |  |  |